# Experiment No.1

# Part 1

# Boiler/Steam Generator Description and Application

# Boiler/Steam Generator: Is a device that used to generate steam.

# Heat Sources:

- Burner

- Solar energy

- Nuclear reactor

# Burner

# Burner.flv

# Boiler Types:

# Fire tube Boilers are: Fire tube Boiler.jpg  Fire Tube Boiler.flv

- Relatively inexpensive

- Easy to clean

- Compact in size

- Available in sizes from 600,000 btu/hr (175 kW) to 50,000,000 btu/hr (14,500 kW)

- Easy to replace tubes

- Well suited for space heating and industrial process applications

# Disadvantages of Fire tube Boilers include:

- Not suitable for high pressure applications 250 psig (17 bars) and above

- Limitation for high capacity steam generation

Water tube Boilers are: ..\Ex Marcet\PowerPlant.exe     Water Tube Boiler.jpg

- Available in sizes that are far greater than the fire tube design. Up to several million pounds per hour of steam.

- Able to handle higher pressures up to 5,000 psig (350 bars).

- Have the ability to reach very high temperatures

# Disadvantages of the Water tube design include:

- High initial capital cost

- Cleaning is more difficult due to the design

- Physical size may be an issue

# Steam Applications:

- Power Generation   ..\Ex Marcet\Steam.gif

- Industrial Application

- Food Factories

- Textile Factories

- Chemical Factories

# Part 2

# Simulator with Controls and Fault Boiler Generation

# Introduction:

This unit has been designed to make available to the students a working model simulating all the factors governing the use, the operation, maintenance and repair of a steam generating system

The simulator has been fitted with all the typical control and adjustment components as are normally employed in industrial boilers of this type, and, in particular, with:

|  | A mixed gas/oil burner; |
| --- | --- |
|  | Three different types of level controls; |
|  | Modulation and safety pressure switches; |
|  | Failure generating panels; |
|  | Synoptic panels with connectors and indicator lamps; |
|  | Electrical fault-finding circuit. |

The boiler body is made of transparent material to enable the students to observe the behavior of the hydraulic phenomena taking place inside the boiler and that of the various controls.

The electrical control and management board, with the synoptic panel and the failure generator at the front, is fixed to the structure of the boiler.

The Device Component

View of the system

1. Electrical control panel

2. Water tank with 100 l. capacity

3. Combined gas/oil burner

4. Mechanical type level control

5. Pressure control manometer

6. Safety valve

7. Max./min. level probe

8. 3-probe electronic level control

9. Magnetic type level control

10. Bunching steam tank

11. Reed contact type level control

- IG General switch

- F1÷5 Fuses

- TP 1÷8 Connectors for electric tests

- Min. level (TP6/7) / Minimum level in the boiler

- Pressure (TP7/8) / Pressure in the boiler

- Min. level (TP3/4) / Minimum level in the supply tank

- Max. level (TP4/5) / Max. level in the boiler

- Water feed pump

- Relief valve

- Steam outlet

- P Manometer

- S1 Burner selector

- Flame failure reset

- Flame failure

- Gas burner / Gas burner synoptic panel

- Oil burner / Oil burner synoptic panel

12. Pedal operated pump for boiler pressure simulation

13. Water recirculation pump

14. Pressure accumulator

15. Working pressure switch

16. Maximum pressure with manual reset pressure switch

17. Working thermostat

18. Gas minimum pressure switch

19. Water recirculation valve

20. Discharge valve

21. Gas feed solenoid valve

Fault simulation panel

This is located to the right of the electric panel and it accommodates twenty switches, each of them having a different function, which produce different operating anomalies by opening or short circuiting the electric nodes.

The effects of the anomalies change depending on the type of burner used (whether gas or oil fuelled). The table lists the different switches and their specific functions.

| Switch | Functions | Anomalies |
| --- | --- | --- |
| 1 | Photocell cut out | Burner blocked |
| 2 | Gas min. pressure switch | Burner blocked |
| 3 | Electrodes short circuited | Burner blocked |
| 4 | Fan motor cut out | Burner will not start |
| 5 | Transformer cut out | Burner blocked |
| 6 | Oil solenoid valve burnt out | Burner blocked |
| 7 | Gas solenoid valve burnt out | Burner blocked |
| 8 | Working pressure switch open | Burner stopped |
| 9 | Maximum pressure switch open | Burner stopped |
| 10 | Water pump not working | Water level low |
| 11 | Mechanical level switch | Pump stopped |
| 12 | Magnetic level switch | Pump stopped |
| 13 | Reed relay level switch | Pump stopped |
| 14 | Electronic level switch | Pump stopped |
| 15 | Minimum level in boiler | Burner stopped |
| 16 | Maximum level in boiler | Pump stopped |
| 17 | Water pump fuse | Pump stopped |
| 18 | Burner fuse | Burner stopped |
| 19 | Burner inlet air pressure switch | Burner blocked |
| 20 | Working thermostat | Burner stopped |

# Text boxes

Liquid Water